## Instructions
Instructions for Energy Code Analysis Checklist v1
When compliance is sought using the performance path of ASHRAE 90.1-2022 Standard this Code Analysis Checklist shall accompany all Commercial Building Permit Plan Submittals which are subject to the requirements of the Standard inclusive of all other documentation, forms, calculations, specifications and certifications. This ASHRAE Code Analysis Checklist shall be submitted indicating sheet, page or section numbers associated with the code provisions of your chosen path of compliance. Space has been provided to input comments as needed for each code provision such as, exceptions, specification notes or other pertinent narratives.
All energy compliance documentation must be signed, sealed and dated by the appropriate design professional.
As you move through the checklist you must provide a response for each section with a Y or N to indicate whether the code provision applies to the scope of work for your project.
Once you have completed this checklist fully upload it into the "Documents" folder in ProjectDox along with all the supporting documents such as load calculations, COMCheck, product specifications, Commissioning Plans, etc. Please name each supporting document clearly when uploading to the Documents folder. Do not print the load calculations and COMCheck on the drawings.
Go to the tab 'ASHRAE' for preparing the mandatory compliance checklist
1. Fill out the energy code analysis checklist completely. Provide supporting documents to demonstrate code compliance.
2. Provide the remarks in the ""Explanation for Not Applicable and/or Explanation for Flag"" column."

## ASHRAE
Energy Code Analysis Checklist - Mandatory Requirements of ASHRAE 90.1 - 2022
ASHRAE 90.1 Section | Requirement | Applies Y/N | Plan/Spec Reference - page number/section | Explanation for Not Applicable and/or Explanation for Flag
Mandatory Compliance
4.2.2 | Compliance Documentation
4.2.3 | Labeling of Material and Equipment
4.2.4, 4.2.5 | Inspections, V & T, and Commissioning
Building Envelope - Air Leakage
5.4.3.1 | Whole-building air leakage testing is required for a new buildings that is less than 10,000 ft² For all other situations, either perform whole-building air leakage testing or provide continuous air barrier.
5.4.3.2 | Continuous air barrier design and installation: a. Components b. Joints, interconnections, and penetrations c. Extent of the continuous air barrier d. To resist positive and negative pressures from wind, stack effect, and mechanical ventilation e. To wrap, seal, caulk, gasket, or tape in an approved manner
5.4.3.3 | Weather seals installed on all loading dock cargo doors.
5.4.3.4 | Vestibules and revolving doors are installed and meet exterior envelope requirements. Doors have self-closing devices.
5.4.3.4.5 (EX 13-24 Amendment) | Section 5.4.3.4.5. Door Switches. Any conditioned space with a door, including doors with more than one-half glass, opening to the outdoors shall be provided with controls that, when any such door is open: a. disable mechanical heating or reset the heating set point to 55 F or lower within five minutes of the door opening; and b. disable mechanical cooling or reset the cooling set point to 90 F or greater within five minutes of the door opening. Mechanical cooling may remain enabled if outdoor air temperature is below space temperature. Exceptions: 1. building entries with automatic closing devices; 2. any space without a thermostat; and 3. loading docks
Building Envelope - Insulation
5.8.1.1 | Building envelope insulation is labeled with R-value or insulation certificate has been provided listing R-value and other relevant data.
5.8.1.2 | Installation shall be in accordance with manufacturer's requirements: below-grade wall, above-grade wall, slab edge, floor, roof.
5.8.1.3 | Blown or poured loose-fill insulation is installed only where the ceiling slope is <= 3:12.
5.8.1.4 | Eaves are baffled to deflect air to above the insulation.
5.8.1.5 | Insulation is installed in a permanent manner in substantial contact with the inside surface separating conditioned space from unconditional space.
5.8.1.6 | Heating, ventilating, and air-conditioning equipment and other equipment shall be recessed in such a manner as not to affect the adjacent insulation.
5.8.1.7 | Exterior insulation protected against damage, sunlight, moisture, wind, landscaping and equipment maintenance activities at 5.8.1.7.1 Attics & mechanical rooms 5.8.1.7.2 Foundation vents, etc. 5.8.1.7.3 In ground contact
5.8.1.10 | Joints in rigid insulation where two or more layers of rigid insulation board are used.
Building Envelope - Fenestration and Doors
5.8.2.1, 5.8.2.2, 5.8.2.3 | Rating of fenestration products and labeling of fenestration and door products. Manufacturer's instruction for installation.
5.8.2.4, 5.8.2.5, 5.8.5.6 | Fenestration products rated (U-factor, SHGC, and VT) in accordance with NFRC 100 or energy code defaults are used.
5.9 | Verification, testing, and commissioning
Heating, Ventilating, Air Conditioning and Motor Systems
6.4.1.1 6.4.1.2 | Minimum equipment efficiencies meet the requirements of Table 6.8.1-1 through Table 6.8.1-21
6.4.1.4, 6.4.1.5 | HVAC equipment efficiencies are verified and provided in the plan. (Use SEER2/HSPF2 in lieu of SEER/HSPF)
6.4.2.1 | Heating and cooling system design loads for the purpose of sizing systems and equipment is determined in accordance with ANSI/ASHRAE/ACCA Standard 183.
6.4.2.2 | Pump differential pressure (pump head) for the purpose of sizing pumps.
6.4.3, 6.4.3.1.1 | HVAC System Controls and Diagnostics. Heating and cooling to each zone is controlled by a thermostat control.
6.4.3.1.2 | Thermostatic controls have a 5 °F deadband.
6.4.3.2 | Temperature controls have setpoint overlap restrictions.
6.4.3.3, 6.4.3.3.1 | Off-hour Controls. HVAC systems are equipped with at least one automatic shutdown control.
6.4.3.3.2 | Setback controls allow automatic restart and temporary operation as required for maintenance.
6.4.3.3.3 | Systems with setback controls and DDC include optimum start controls. Optimum start algorithm considers mass radiant slab floor temperature.
6.4.3.3.4 | Zone isolation devices and controls are provided.
6.4.3.3.5 | Hotels/motel w/ > 50 guest rooms have automatic controls for the HVAC equipment serving each room.
6.4.3.4, 6.4.3.4.1 | Ventilation System Controls. Stair and elevator shaft vents have motorized dampers that automatically close during normal building operation and are interlocked to open as required by fire and smoke detection systems.
6.4.3.4.2, 6.4.3.4.3 | Shutoff damper controls and damper leakage. Outdoor air and exhaust systems have motorized dampers that automatically shut when not in use and meet maximum leakage rates.
6.4.3.4.4 | Ventilation Fan Controls. Ventilation fans >0.75 hp have automatic controls to shut off fan when not required.
6.4.3.4.5 | Enclosed parking garage ventilation has automatic contaminant detection and capacity to stage or modulate fans to 50% or less of design capacity.
6.4.3.5 | Heat pump controls prevent supplemental electric resistance heat from coming on when not needed.
6.4.3.6 | Humidification and Dehumidification Control. 6.4.3.6.1 Dehumidification 6.4.3.6.2 Humidification 6.4.3.6.3 Control Interlock
6.4.3.7 | Freeze protection systems, such as heat tracing of outdoor piping and heat exchangers, including self-regulating heat tracing, shall include automatic controls.
6.4.3.8 | Demand Control Ventilation (DCV). Ventilation controls for High-Occupancy Area is provided with DCV.
6.4.3.9 | Heating for vestibules and air curtains with integral heating include automatic controls that shut off the heating system when outdoor air temperatures > 45F. Vestibule heating and cooling systems controlled by a thermostat in the vestibule with heating setpoint <= 60F and cooling setpoint >= 80F.
6.4.3.10 | Direct digital controls (DDC) requirements.
6.4.3.11.1 | Electric motor driven chilled-water plants have measurement devices installed and measure the electricity use and efficiency.
6.4.3.11.2 | Electric-motor-driven chiller system electricity use and efficiency are trended every 15 minutes and graphically displayed, including hourly, daily, monthly, and annual data. Data are preserved for 36 months or more.
6.4.3.12 | Air economizer has a fault detection and diagnostics (FDD) system (see details for configuration and operational requirements).
6.4.4.1.1 | Insulation exposed to weather protected from damage. Insulation outside of the conditioned space and associated with cooling systems is vapor retardant.
6.4.4.1.2 | HVAC ducts and plenums are insulated per Table 6.8.2.
6.4.4.1.3 | HVAC piping is insulated per Tables 6.8.3-1 and 6.8.3-2.
6.4.4.1.4 | Sensible Heating Panel Insulation. Thermally ineffective panel surfaces of sensible heating panels have insulation >= R-3.5. Adjacent building envelope insulation counts toward this requirement.
6.4.4.1.5 | Radiant floor heating. Bottom surface of floor structures incorporating radiant heating insulated to >=R-3.5. Adjacent building envelope insulation counts toward this requirement.
6.4.4.2.1 | Duct Sealing Ductwork and all plenums with pressure class ratings are to be constructed to Seal Class A. All connections are to be sealed. All duct pressure class ratings are designated in the design documents.
6.4.4.2.2 | Duct Leakage Tests => 25% of the total installed duct of the representative sections are for the designated pressure class are to be tested.
6.4.5 | Walk-In coolers and Walk-in freezers Site-assembled or site-constructed walk-in coolers and walk-in freezers shall conform to the requirements from 'a' through 'm'.
6.4.6 | Refrigerated display case shall conform to the requirements from 'a' through 'd'.
6.4.7 | Liquid-to-Liquid Heat Exchangers
6.7.3 | Completion Requirements 6.7.3.1 Record documents/furnished HVAC as-built drawings, and 6.7.3.2 O&M Manuals shall be submitted to the building owner or owner's designated representative.
6.7.3.3 | System Balancing Construction documents shall require that a written balance report be provided to the building owner or the designated representative of the building owner for HVAC systems serving zones with a total conditioned area exceeding 5000 ft²
6.9 | Verification, testing, and commissioning
Service Water Heating Systems
7.4.1 | Service water heating system design loads
7.4.2 | All water-heating equipment, hot-water boilers used solely for heating potable water, pool heaters, and hot-water storage tanks meet the criteria listed in Table 7.4-1. Exception to 7.4.2
7.4.3 | Service water heating system piping insulation meets the requirements of Table 7.4-1 a. Recirculating system piping b. The first 8 ft of outlet piping c. The first 8 ft of branch piping d. The make-up water inlet piping e. Hot-water piping f. Piping that is externally heated
7.4.4.1 | Temperature controls installed on service water heating systems (<=120ºF to maximum temperature for intended use).
7.4.4.2 | Automatic time switches installed to automatically switch off the recirculating hot-water system or heat trace.
7.4.4.3 | Public lavatory faucet water temperature <=110°F.
7.4.4.4 | Circulating pump controls
7.4.5.1 | Pool heaters are equipped with on/off switch and no continuously burning pilot light.
7.4.5.2 | Pool covers are provided for heated pools and pools heated to >90°F have a cover >=R-12.
7.4.5.3 | Time switches are installed on all pool heaters and pumps.
7.4.6 | Heat traps installed on non-circulating water heating storage water tanks.
7.9 | Verification, testing, and commissioning
Power Systems
8.4.1 | Feeder conductors and branch circuits combined shall be sized for a maximum of 5% voltage drop total.
8.4.2 | Automatic receptacle control to conform the requirements from 'a' through 'c'.
8.4.3 | New buildings have electrical energy use measurement devices installed. Where tenant spaces exist, each tenant is monitored separately. In buildings with a digital control system the energy use is transmitted to control system and displayed graphically.
8.4.3.1 | Monitoring: a. Total electrical energy, b. HVAC systems, c. Interior lighting, d. Exterior lighting, e. Receptacle circuits, f. Refrigeration systems
8.4.3.2 | Recording and reporting the electrical energy use if 1. building > 25,000 ft² 2. individual tenant spaces < 10,000 ft² 3. residential buildings with < 10, 000 ft²of common area.
8.4.4 | Low-voltage dry-type distribution transformers
8.7.3 | Completion Requirements 6.7.3.1 Record documents/furnished HVAC as-built drawings, and 6.7.3.2 O&M Manuals shall be submitted to the building owner or owner's designated representative.
8.9 | Verification, testing, and commissioning
Interior Lighting Power and Lighting Controls
9.4.1.1 | All of the lighting control functions prescribed in Table 9.5.2.1, for the appropriate space type, are to be installed. Mandatory lighting controls (labeled as 'REQ') and optional choice controls (labeled as 'ADD1' and 'ADD2') are implemented following 9.4.1.1 a through 9.4.1.1 d.
9.4.1.1e, 9.4.1.1f | Automatic daylight responsive controls for primary sidelighted and toplighting area when lighting power >= 75 W and for secondary sidelighted area when >= 150 W
9.4.1.1 g 9.4.1.1 h | Automatic reduction controls and maximum delay-time for turn-off lights.
9.4.1.1 i 9.4.1.1 j | Time-switch controls: scheduled shutoff, 7-day weekly and holiday program, and maximum override hours.
9.4.1.2a | Parking garage lighting is equipped with automatic shutoff controls per 90.1 Section 9.4.1.1(i).
9.4.1.2b | Parking garage luminaire power is automatically reduced by >= 50% when zone < 3600 ft² has no occupancy after 10 minutes.
9.4.1.2c | Parking garage daylight transition zone lighting shall be separately controlled to automatically reduce the lighting to no more than the general light level from sunset to sunrise.
9.4.1.2d | The power to any lunimaire within 20 ft of perimeter wall openings totaling at least 24 ft² shall be automatically reduced through continuous dimming in response to avaiable daylight.
9.4.1.3 | Special applications have separate lighting control devices for specific uses installed and specified. a. 1)Display or accent lighting, 2). Lighting in display cases, b. Guestrooms, c. Supplemental task lighting
9.4.3 | Dwelling units. At least 75% of the permanently installed luminaire shall use lamps with efficacy of at least 75 lm/W or have a total luminaire efficacy of at least 50 lm/W
9.4.4 | Horticultural lighting
Exterior Lighting
9.4.1.4 | Automatic lighting controls for exterior lighting installed. Lighting for exterior applications not exempted in Section 9.1 shall meet the following requirements: a. Off control, b. Daylight off control, c. Scheduled off control. d. Scheduled light reduction control. e. Occupancy-sensing light reduction control
9.4.2 | Exterior lighting power
All Lighting
9.9 | Verification, testing, and commissioning
Other Equipment - Electric Motors General purpose small electric motors with a rated motor power of 0.25 hp or more, and less than or equal to 3 hp, shall have a minimum average full-load efficiency that is not less than as shown in 90.1 Table 10.8-3 for polyphase small electric motors and 90.1 Table 10.8-4 for capacitor-start capacitor-run small electric motors and capacitor-start induction-run small electric motors. Fire pump electric motors shall have a minimum nominal full-load efficiency that is not less than that shown in 90.1 Table 10.8-5.
10.4.1 | Electric motors Exception to 10.4.1
10.4.2 | Service water pressure booster system
10.4.3 | Elevators are designed with the proper lighting, ventilation power, and standby mode.
10.4.4 | Escalators and moving walks
10.4.5 | Air curtains
10.4.7 | Whole-building energy monitoring
10.4.8 | Pumps Exception to 10.4.8
10.9 | Verification, testing, and commissioning
End of the Checklist