Bill No.  	23-18

Concerning: 	Fire Safety – Carbon Monoxide Alarm

Revised:  	9/24/2018	 Draft No. 	4

Introduced:  	June 19, 2018

Enacted:  	October 2, 2018

Executive:  	October 11, 2018

Effective:  	July 1, 2019

Sunset Date:  	None

Ch. 	23	, Laws of Mont. Co.  	2018

County Council

For Montgomery County, Maryland

Lead Sponsor: Councilmember Rice

Co-Sponsor: Councilmember Elrich

AN ACT to:

- require the owners of certain dwelling units to install and maintain a carbon monoxide alarm or detector; and

- generally amend County [[fire safety]] laws related to housing and building maintenance standards.

By adding

Montgomery County Code

Chapter [[22, Fire Safety Code]] 26, Housing and Building Maintenance Standards

Section [[22-99]] 26-8A

Boldface	Heading or defined term.

Underlining	Added to existing law by original bill.

[Single boldface brackets]	Deleted from existing law by original bill.

Double underlining 	Added by amendment.

[[Double boldface brackets]]	Deleted from existing law or the bill by amendment.

*   *   *	Existing law unaffected by bill.

The County Council for Montgomery County, Maryland approves the following Act

Sec. 1. Section [[22-99]] 26-8A is added as follows:

[[22-99]] 26-8A. Carbon monoxide alarm or detector required.

(a)	Applicability. The provisions of this Section apply to any occupied single-unit, two-unit, and townhouse unit, as defined in Chapter 59, for which a building permit was issued before January 1, 2008.

(b)	Required.

(1)	The owner of each occupied single-unit, two-unit, and townhouse dwelling unit containing a fuel burning appliance or attached garage must install [[a]] carbon monoxide [[alarm in a central location outside of each sleeping area within a dwelling containing a fuel burning appliance]] detection and warning equipment.

(2)	Carbon monoxide alarms or detectors must be installed as follows:

(A)	outside of each separate dwelling unit sleeping area and in the immediate vicinity of the bedrooms; and

(B)	on every occupiable level of a dwelling unit, including basements, excluding attics and crawl spaces.

(3)	A carbon monoxide alarm or detector must:

(A)	[[comply with Underwriters Laboratories standard 2034]] be located on the wall, ceiling, or other location as specified in the manufacturer’s published instructions that accompany the unit; and

(B)	be installed and maintained under NFPA 720 [[and the manufacturer’s instructions]].

[[(b)]] (c) Equipment.

(1)	Single station carbon monoxide alarms.

(A)	A single station carbon monoxide alarm must be battery operated or must receive its primary power from the building wiring system.

(B)	A plug-in device may satisfy this requirement if it is securely fastened to the structure and installed as directed by the manufacturer’s installation instructions.

(C) 	A hard wired or plug-in carbon monoxide alarm must be equipped with battery back-up.

(2)	Combination smoke detector/carbon monoxide alarms.

(A)	A carbon monoxide alarm may be combined with a smoke detector if the device complies with this Section, Section 22-96, and applicable State law.

(B)	A combination smoke detector/carbon monoxide alarm must receive its primary power from the building wiring when that wiring is served from a commercial source, and when primary power is interrupted, must receive power from a battery.

(C)	A combination smoke detector/carbon monoxide alarm must have permanent wiring.  The only disconnecting switch allowed is that which is required for over-current protection. Smoke alarm features of a combination smoke detector/carbon monoxide alarm must be interconnected.

[[(c)]] (d) Exceptions. A dwelling unit that does not itself contain a fuel-burning appliance or have an attached garage, but is located in a building with a fuel-burning appliance or an attached garage, does not need to be equipped with a carbon monoxide alarm if:

(1)	the sleeping unit or dwelling unit is located more than one story above or below any story which contains a fuel-burning appliance or attached garage;

(2)	the sleeping unit or dwelling unit is not connected by ductwork or ventilation shafts to any room containing a fuel-burning appliance or to an attached garage; and

(3)	the building is equipped with a common area carbon monoxide alarm system, which includes carbon monoxide detectors and audible notification appliances, installed and maintained in a manner that satisfies this Section and NFPA 720.

[[(d)]] (e) Orders to install; penalty.

(1)	If [[the State Fire Marshal or local investigating authority]] an enforcing agency finds that a dwelling unit does not have a carbon monoxide detector as required under this Section, the [[State Fire Marshal or local investigating authority]] enforcing agency must order the owner to install a carbon monoxide alarm or detector [[within 15 days of the date of the order]] under Section 26-12.

(2)	Notwithstanding Section [[22-22]] 26-16, a violation of this Section is a Class C violation.

Sec. 2. Effective Date.

Section [[22-99]] 26-8A, as added by Section 1 of this Act, takes effect on July 1, 2019.

Approved:

/s/										10/5/18

Hans Riemer, President, County Council					Date

Approved:

/s/										10/11/18

Isiah Leggett, County Executive							Date

This is a correct copy of Council action.

/s/										10/11/18

Megan Davey Limarzi, Esq. Clerk of the Council				Date